KURUMAN TAXI RANK

ELECTRICAL INSTALLATIONS

PART 2 : SUPPLEMENTARY SPECIFICATION

I N D E X

Clause 	Description	Page

1.		General 	  10

2.		Scope of Contract 	  10

3.		Electricity Supply 	  11

4. 		Low Voltage Distribution Boards………………………………………………...11

5.		Low Voltage Cables 	  11

6.		Conduit 	  11

7.		Earthing 	  12

8.		Project Program and Phasing of the Delivery of Materials 	  12

9.		Luminaires 	  12

10.		Maintenance Requirements 	  13

11.		Load Balancing 	  13

12.		Items for Approval 	  13

13.		Contract Administration, Completion, Testing and Commissioning 	  13

14.		Power Points 	  17

15.		Switched Socket Outlets	  17

16.		Mounting Heights of Luminaires & Sockets	  17

17.		Lightning Protection and Earthing	  17

18.		Trenching	  18

KURUMAN TAXI RANK

ELECTRICAL INSTALLATIONS

PART 2 : SUPPLEMENTARY SPECIFICATION

1.	GENERAL

This Project Specification must be read as an addendum to the General Specification for electrical works.

This Project Specification together with the drawings describe the scope of works to be executed in terms of this documentation.

2. SCOPE OF CONTRACT

The scope of the electrical works described in detail in this document and drawings covers the supply, delivery, off-loading, storage, installation, commissioning, testing, handing over and free maintenance for the period stated in the tender document of all specified equipment and materials for the Electrical Installation required for the Kuruman Taxi Rank in Kuruman, Ga-Segonyana Local Municipality.

The project sites location is  27°27'21.57"S, 23°25'59.79"E.

The electrical materials to be installed, per site, include the following with their all their accessories:

- 20mm diameter Galvanised Steel conduit and round steel conduit boxes,

- 25mm PVC conduits and round PVC conduit boxes,

- 100mm x 100mm x 50mm and 100mm x 50mm x 50mm galvanized steel conduit boxes,

- 50mm diameter and 110mm diameter ribbed cable sleeves,

- Building light fittings, light switches, power skirting, socket outlet, photocell, occupancy sensor,

- Streetlights on street light poles,

- Electrical wiring and cabling,

- Indoor and outdoor distribution Boards,

- Underground Power cables.

The installation shall be suitable for operation at Kuruman, at an altitude of approximately 1300m above sea level with an average maximum atmospheric temperature of 31.2 C and an average minimum temperature of 13.5 C.

The onus is on the tenderer to ascertain any local conditions or peculiarities which might affect the contract, and which are not shown on the drawings.

3. ELECTRICITY SUPPLY

The electricity supply shall be 400V 50Hz, provided by the Ga-Segonyana Local Municipality from their     existing 1MVA 11kV/400V brick substation, which is in the vicinity of the taxi rank.

It shall be the responsibility of the contractor to make arrangements with the municipality for the electrical supply connection.

4. LOW VOLTAGE DISTRIBUTION BOARDS

The scope of this portion of the works will installation of new DBs (distribution boards).

Busbar stubs must be provided where more than one conductor terminates on equipment.

Earth conductors must be fastened with two screws and shoes to earth bars.

| DB | Indoor/Outdoor | Mounting | Lock type | Purpose/ load |
| --- | --- | --- | --- | --- |
| DB-BUS | Indoor | Flush recessed | Handle | Bus Ticket Office, SLs |
| DB-1 | Indoor | Floor standing | Handle | FF, Lift, DB-2, DB-4, |
| DB-2 | Outdoor | Surface | Internal lock | Stalls, lights, DB-3, DB-5 |
| DB-3 | Outdoor | Surface | Internal lock | Stalls, lights |
| DB-4 | Outdoor | Surface | Internal lock | Toilets, Fire Water Pumps |
| DB-5 | Outdoor | Surface | Internal lock | Stalls, lights, DB-6, SLs |
| DB-6 | Outdoor | Surface | Internal lock | Stalls, lights, SL, DB-7 |
| DB-7 | Outdoor | Surface | Internal lock | Stalls, SLs |

5. LOW VOLTAGE CABLES

The LV cables shall be PVC insulated, PVC bedded, SWA with ECC (tinned copper wires), PVC sheathed, 600V/1000V copper cable, manufactured to SANS 1507-3.

The motor feeder cable for each site shall be an annealed copper conductor, PVC insulated, SWA, PVC insulated, and PVC sheathed.

All low voltage cables terminating in distribution boards shall be terminated with “Pratley” glands and holes for glands shall be cut with hole saws of the correct size to allow for proper tightening of the gland on the switchboard frames.

Although cables have been specified and lengths included in the Bills of Quantities, it should be

noted that all cable lengths shall be measured no site and shall only be ordered upon approval by

the Engineer.

6. CONDUIT

SABS (SANS 533, SANS 1210, SANS 97 etc.) approved conduits will be used throughout the contract.

All conduit runs must be planned properly and co-ordinated with other services.

Specific service routes where conduit for various services are grouped, must be used.

Unsightly and unplanned conduit installations will not be accepted and will be replaced by the contractor at his own expense.

Under the Taxi Rank slab, conduits exiting from DBs (i.e.DB-2,DB-3, DB-5, DB-6 and DB-7) shall run in the walls towards the slab. These will exist the wall and run surface on the slab soffit.

7. EARTHING

Earthing of the installation shall be in accordance with the Act and the earthing standard.

On the main earth bars, all equipment are to be properly earthed and bonded.

During installation of the cables and associated earth conductors, the contractor shall take note of

copper theft, which is at present prevalent in the building industry, and as such he shall take all

precautions to ensure that theft is minimised.

8. PROJECT PROGRAM AND PHASING OF THE DELIVERY OF MATERIALS

In terms of the contract conditions, the electrical contractor shall liaise with the other contractors

and arrange his own program in accordance with the program for the building, in order that the

electrical installation of the different sections is completed when required.

Careful preplanning of material deliveries by the electrical contractor will be required and

supplier’s delivery times will be crucial, not only to ensure that this requirement is met, but

also to ensure that the construction activities are not delayed.

9. LUMINAIRES

Tenderers shall allow for all luminaires listed in the BoQ and shown on the drawings.

When the term “equivalent approved” is not used in the specification, the tenderers shall have

no choice but to install the specific Luminaires as specified.

Should a tenderer opt to supply an alternative light fitting brand instead of what is specified, such

a tenderer shall supply technical information with his/her tender which shows how their choice of

fitting is equivalent to the one specified. Moreover, the sad tenderer shall also submit a lighting

study (simulation) which uses the said equivalent, with their tender.

All luminaries shall be complete with lamps, indicator lamps, ballasts, chokes, control gear and all

other accessories required to make the luminaries fully operative.

All luminaries shall be equipped with an earth terminal and shall be properly earthed.

The Contractor shall be responsible for the purchasing, taking delivery, storing, installation,

aiming, adjustment, testing and commissioning of all luminaries specified including all necessary

mounting accessories, bracket, poles, stirrups, base plates, etc. and including any necessary

excavation and backfilling.

The internal wiring shall consist of flexible stranded copper conductors of not less than 0.5 mm²

with suitable heat-resisting insulation to SABS 529.  A terminal block shall be fitted to each

luminaire.

Luminaires shall not cause radio or television interference in accordance with Posts and

Telecommunications requirements.

Luminaires shall be designed to prevent excessive temperatures and components and materials

shall be selected so that they are not adversely affected by the operating temperature.

The voltage rating and lamp wattage shall be clearly and indelibly marked on control gear.

All luminaires shall be of LED type, shall surge protection and shall be flicker-free even under a

digital camera.

The wattage and type of lamp suitable for use in the luminaire shall be clearly marked on the base

of the luminaire close to the lampholder.

The contractor is to note that in the case of board and acoustic tile ceilings, i.e. as opposed to

concrete slabs, close co-operation with the Building Contractor is necessary to ensure that as far

as possible, the luminaries are symmetrically positioned with regard to the ceiling pattern.

Where luminaries are mounted on ceilings consisting of panes, care has to be taken that the work

Is performed symmetrically.  Conduit work above false ceilings shall be fully co-ordinated in level,

plan and sequence of installation with the Building and Ceilings Contractor, the Air Conditioning

Contractor and any other Contractor installing services in the false ceilings.

Luminaires narrower than 225mm shall be fixed at the outlet point and at two further positions.

Luminaires wider than 225mm shall have four fixings exclusive of the outlet point.

Conduits shall be screwed directly into all weatherproof luminaries and other outside lights.  No

outlet boxes are permitted.  The conduit shall be installed in such a way that it falls from the wall

to the luminaries at an angle.

The bases of all luminaries shall be installed after the first coat of paint has been applied.  The

luminaries shall then be left until the painting has been finished, after which the Contractor shall

complete the installation and adjusting of the luminaries.

All luminaires shall be fixed and suspended in accordance with the manufacturer’s requirements

and as specified.

10. MAINTENANCE REQUIREMENTS

The maintenance period as per agreement shall apply. It is however a further requirement of this

contract that three months after handover of the installation, all faulty lamps and tubes shall be

replaced by the contractor at no additional cost to the client.

It is a further requirement of this contract that any tenderer not situated within the

Ga-Segonyana Local Municipality, shall make arrangements with local contractors to perform the

maintenance function on his behalf during the maintenance period.  Details of this arrangement

shall be included with the tender that is submitted by such a tenderer.

It should furthermore be noted that the maintenance requirements entail normal working hours

(8-hour call-out 5 days a week) during the maintenance period and in all cases, as

response time of less than one hour is required.

11. LOAD BALANCING

It shall be the responsibility of the appointed contractor to ensure that the loads are evenly distributed over the three phases.

12. ITEMS FOR APPROVAL

Where this specification refers to a specific brand name or "similar and equivalent" or "Other approved type" and alternative equipment is offered in lieu of that specified, then written approval must be obtained from the Engineer before such equipment is installed.

The right is reserved to reject any equipment which does not, in the opinion of the Engineer, conform to specification or which is of an inferior grade.  Should such equipment be rejected, the contractor shall at his own expense provide for alternative equipment and tenderers are thus warned to ensure that all equipment offered is in strict accordance with the requirements of this specification.

In certain cases the contractor may be required to submit samples and where necessary, tests will be performed to establish the quality of the material offered.

13. CONTRACT ADMINISTRATION, COMPLETION, TESTING AND COMMIS-SIONING

13.1 QUALITY CONTROL DURING THE EXECUTION OF THE CONTRACT

Day by day inspections of the Works shall be carried out by the Contractor or his authorized representative to ensure that all work is executed in accordance with the drawings, specifications and regulations.  These inspections will be monitored by the Engineer or his duly authorized representative.

If the quality of the installation suffers due to a lack of supervision, then the Engineer will appoint a site agent to ensure that a high standard of workmanship is maintained.  The full cost of such a step shall be for the contractors account.

13.2 STANDARD OF WORKMANSHIP

All installation work in this contract is to be executed by qualified electricians and cable jointers in accordance with modern techniques.  The Engineer shall have the right to reject any work which does not meet with his approval or which is not in accordance with standard practice.

13.3 MAINTENANCE OF AS-BUILT DRAWINGS

During execution of the contract the contractor shall update the drawings daily with all the relevant information.

At the end of the contract and prior to handover being accepted, the contractor shall prepare as-built drawings of the installation.  These drawings shall be a set of the latest drawings issued by the Engineer on which the contractor shall highlight all changes.  The contractor shall take great care to ensure that all underground services are shown in the correct places.

The contractor shall also issue three (3) sets of any other drawings, wiring diagrams, service and instruction manuals for equipment supplied by him and these will have to be acceptable to the Engineer prior to handover being approved.

13.4 SETTING OF PROTECTIVE DEVICES AND CONTROLS

All protective devices shall be correctly installed by the Contractor to the approval of the Engineer before the installation is energized.

Data, with regard to all commissioning documentation and diagrams of all circuits, are to be provided for approval prior to their installation.  These diagrams shall include:

Wiring diagrams

Schematic wiring diagrams

The correct operation of all circuits is to be verified on site in the presence of the Engineer or his authorized Representative.

13.5	PRELIMINARY TESTING OF MAJOR EQUIPMENT

All items of major equipment are, where feasible, to be factory tested prior to delivery to site, and results of such tests, in a format to be agreed in advance, are to be produced before the equipment is delivered.

All such tests are to be in accordance with the relevant codes of practice, and with any other requirements as set out in this document.

13.6 COMPLETION OF INSTALLATION

Before the commencement of any test or commissioning procedures, the Contractor is to ensure that all nuts and bolts are securely fastened, and that paintwork on all items supplied has been touched up where damage has occurred.

13.7 INSPECTION AND TESTING

On completion of the entire installation or any particular section thereof, as may be decided by the Engineer, tests shall be carried out in full accordance with the current edition of the "Code of Practice for the Wiring of Premises", in the presence of the Engineer or his authorized Representative.

The Contractor should note that, where applicable, at least the following tests must be carried out:-

Insulation resistance test (Megger).

Continuity test

Loop Line Earth Impedance test

Polarity test

Earth Leakage Circuit Breaker test

Earth termination test.

Any further tests as deemed necessary by the Engineer.

All instrumentation necessary for testing shall be provided by the Contractor.

The results of the above tests must be clearly recorded, signed and handed to the Engineer or his authorized Representative together with a Certificate of Compliance and any other form or forms as required by the Client.

13.8 DOCUMENTATION

The following documentation shall be required:-

- Set of schematic wiring and function diagrams.

- Operating and maintenance instructions on equipment.

- Guarantees ceded to the Client.

Once the Engineer has inspected the complete installation and satisfied himself that all testing has been completed and the contract is complete in all respects, will he issue a letter to the Client stating that first delivery has been taken.  Once the retention period has expired, the installation shall be inspected for final delivery.

13.9  LABELLING

All switchgear and equipment installed in the switchboards, plus isolator boxes, cables, etc., shall be clearly labelled as indicated elsewhere in this specification and schedules.

13.10 TRAINING OF INSTITUTIONAL STAFF

Where applicable, allowance is to be made by the Contractor for the training of Institutional Staff in the setting up and operation of the various items of equipment supplied under the contract.

13.11 TESTING AND COMMISSIONING DOCUMENTATION

On completion of the testing and commissioning, the following documents shall be compiled and presented to the Engineer.

- A Certificate of Compliance and other form/s as required by the Engineer and Client.

- Drawings of the installation marked up "As Built" as described elsewhere.

- Completed set of test and commissioning sheets.

14. POWER POINTS

Allow for the installation of power points and equipment as listed in the schedule, indicated on

the drawings.

15. SWITCHED SOCKET OUTLETS

All switch socket outlets must have a rating of 250 Volt 16 Amp, unless otherwise specified.

All switches must meet the requirements of SANS 163, as amended and socket outlets, SANS 164 and 1514, as amended. All the circuits for socket outlets shall be supplied with 4mm² PVC insulated stranded copper wire and 2,5mm² bare copper earth wire.

Each normal triangular 3 pin socket outlet (SANS 164-1) shall be accompanied by a compact 3 pin socket outlet (SANS 164-2), as a separated socket or as a combo.

15.1 DESIGNATED SOCKET OUTLETS

All designated socket outlets must comply with the quality specification and be approved by the Engineer.

The designated switch socket outlet will be of the Red type (with a flat earth pin in the 12 O'clock position – SANS 164-4) and where applicable, for the installation in a power skirting complete with cover plate.

19. MOUNTING HEIGHTS OF LUMINAIRES & SOCKETS

19.1 OUTDOOR

Outdoor wall mounted luminaires must be mounted at as indicated in the drawings.

19.2 INDOOR

Mounting Heights

Socket outlets, light switches and isolators must me installed at AFFL heights indicated on drawings.

17. LIGHTNING PROTECTION AND EARTHING

This item covers the supply, delivery and installation of a complete lightning conductor system

and shall comply in all aspects with the requirements set in the SABS Users' Code 03 of 1985 (as

amended).

IT IS SPECIFIC REQUIREMENT OF THIS CONTRACT THAT THIS PART OF THE

INSTALLATION SHALL BE DONE BY SPECIALISTS WHO ARE CONVERSANT WITH THIS

TYPE OF WORK, AND PREFERBALY WHO ARE A MEMBER OF ELPA (EARTHING AND

LIGHTNING PROTECTION ASSOCIATION).

18. TRENCHING

18.1 GENERAL

The provision of trenches for the laying of cables and the installation of and cable sleeves forms

part of this contract.  All cables and sleeves shall be laid at a depth of 600mm except that sleeves

below the building may be laid at a lesser depth provided that the Engineer is satisfied that no

damage to the sleeves can occur.

The bottom of the trenches shall be of smooth contour and shall have no sharp dips or rises

which may cause tensile forces in the cable during backfilling.

Prior to cable laying, the trench shall be inspected thoroughly and all objects likely to cause

damage to the cables either during or after laying shall be removed.

Where ground conditions are likely to reduce maximum current carrying capacities of cables or

where the cables are likely to be subject to chemical or other damage or electrolytic action, the

Engineer shall be notified before installing the cables and will then advise on the course of action

to be taken.

18.2 DIMENSION OF TRENCHES

Cable trenches for one or two cables or sleeves shall not be less than 300mm wide and need not

be more than 500mm wide.  This dimension shall be valid for the total trench depth.

Where trenches change direction or where cable slack is to be accommodated, the contractor

shall ensure that the requirements of the relevant SABS Specification regarding the bending radii

of cables are met when determining trench widths.

Trench depths shall be determined in accordance with cable laying depths and bedding thickness.

18.3 BEDDING

The bottom of the trench shall be filled across the full width with a 75mm layer of suitable soil sifted through a 6mm mesh and levelled off.

Only sandy clay or loam soil with a satisfactory thermal resistivity (not exceeding 1,5 C m/W) may be used for this purpose.  Sea or river sand, ash, chalk, peat, clinker or clayey soil shall not be used.  The use of crusher sand is acceptable.

Where no suitable soil is available on site, the Electrical Contractor shall import fill from elsewhere and make all the necessary arrangements to do so.  The cost of importing soil for bedding purposes shall be included in the unit rates for excavations.

After cable laying a further layer of bedding shall be provided to extend to 75mm above the cables.

18.4 BACKFILLING

The Electrical Contractor shall not commence with the backfilling of trenches without prior notification to the Engineer so that the cable installation may be checked.  Should the Electrical Contractor fail to give a timeous notification, the trenches shall be re-opened at the Electrical Contractor cost.  Such an inspection will not be unreasonably delayed.

Backfilling shall be undertaken with soil suitable to ensure settling without voids.  The maximum allowable diameter of stones present in the backfill materials is 75mm.

The Electrical Contractor shall have allowed in his tender for the importation of suitable backfill material if required and such costs shall be included in the unit rates for excavations.

The backfill shall be compacted in layers of 150mm and sufficient allowances shall be made for final settlement.  The Electrical Contractor shall maintain the refilled trench at his expense for the duration of the contract.  Surplus material shall be removed from site and suitably disposed of.

On completion of the contract the surface shall be made good to match the surrounding area.

In the case of roadways or paved areas the excavations shall be consolidated to the original density of the surrounding material and the surface finish reinstated.

18.5 MEASUREMENT

Trench excavations shall be measured and paid for as per the unit rate included by Tenderers for

excavations.  In all cases the cost of excavations shall include the total cost of excavating,

bedding, backfilling and making good.

Definitions for the different type of excavations are as follows:

- Earth:	Excavations which can be performed with pick and shovel.

- Soft rock: Excavations where it is clear that compressor operated jack hammers are required to remove the rock and includes for areas where large boulders which must be mechanically moved occur.

- Hard rock: Hard rock will be measured where excavations can only be performed by means of earth moving equipment and/or blasting.